## Sheet1
PIPE SIZING TABULATION SHEET
FITTINGS AND VALVES VELOCITY PRESSURE LOSS METHOD
PIPE SECTION | LOADING UNITS | FLOW RATE | TUBE SIZE | VELOCITY | FITTINGS & VALVES |  |  |  | PIPE SECTION LENGTH | PRESSURE LOSS PER 100 m TUBE | FITTINGS & VALVES PRESSURE LOSS | PIPE SECTION PRESSURE LOSS
[7 empty] | Head loss factor | Pressure loss each m=K*(v2/2g)
Labelled | No | L/s | DN | m/s | No | Type | K | m. head | m | m. head | m. head | m. head
1 | * | 0.1 | 15 | 1.076 |  |  |  | 0 | 2 | 16.858 | 0 | 0.33716
1 | * | 0.1 | 15 | 1.076 | 1 | elbow | 2.2 | 0.12995 |  |  | 0.12995 | 0
1 | * | 0.1 | 15 | 1.076 | 1 | reducer | 1 | 0.05907 |  |  | 0.05907 | 0
2 | 3 | 0.14 | 20 | 0.616 |  |  |  | 0 | 2 | 3.622 | 0 | 0.07244
2 | 3 | 0.14 | 20 | 0.616 | 1 | flow tee | 0.9 | 0.017424 |  |  | 0.017424 | 0
3 | 11 | 0.28 | 20 | 1.232 |  |  |  | 0 | 2 | 12.191 | 0 | 0.24382
3 | 11 | 0.28 | 20 | 1.232 | 1 | flow tee | 0.9 | 0.069696 |  |  | 0.069696 | 0
4 | 13 | 0.3 | 20 | 1.32 |  |  |  | 0 | 2 | 13.769 | 0 | 0.27538
4 | 13 | 0.3 | 20 | 1.32 | 1 | branch tee | 2.1 | 0.18669 |  |  | 0.18669 | 0
5 | 18 | 0.36 | 20 | 1.584 |  |  |  | 0 | 4 | 19.009 | 0 | 0.76036
5 | 18 | 0.36 | 20 | 1.584 | 1 | branch tee | 2.1 | 0.26883 |  |  | 0.26883 | 0
6 | 24 | 0.42 | 20 | 1.848 |  |  |  | 0 | 2 | 24.989 | 0 | 0.49978
6 | 24 | 0.42 | 20 | 1.848 | 1 | flow tee | 0.9 | 0.15682 |  |  | 0.15682 | 0
7 | 27 | 0.44 | 20 | 1.936 |  |  |  | 0 | 1 | 27.144 | 0 | 0.27144
7 | 27 | 0.44 | 20 | 1.936 | 1 | flow tee | 0.9 | 0.17211 |  |  | 0.17211 | 0
8 | 35 | 0.51 | 20 | 2.244 |  |  |  | 0 | 1 | 35.309 | 0 | 0.35309
8 | 35 | 0.51 | 20 | 2.244 | 1 | flow tee | 0.9 | 0.23122 |  |  | 0.23122 | 0
8 | 35 | 0.51 | 20 | 2.244 | 1 | ball valve | 0.27 | 0.069367 |  |  | 0.069367 | 0
[8 empty] | 0 |  |  | 0 | 0
9 |  | 0.48 | 20 | 2.112 |  |  |  | 0 | 3.3 | 31.692 | 0 | 1.0458
9 |  | 0.48 | 20 | 2.112 | 1 | elbow | 1.7 | 0.38688 |  |  | 0.38688 | 0
10 |  | 0.7 | 25 | 1.691 |  |  |  | 0 | 3.3 | 14.71 | 0 | 0.48543
10 |  | 0.7 | 25 | 1.691 | 1 | flow tee | 0.9 | 0.1313 |  |  | 0.1313 | 0
11 |  | 0.88 | 25 | 2.125 |  |  |  | 0 | 3.3 | 22.13 | 0 | 0.73029
11 |  | 0.88 | 25 | 2.125 | 1 | flow tee | 0.9 | 0.20735 |  |  | 0.20735 | 0
12 |  | 1.03 | 32 | 1.556 |  |  |  | 0 | 3.3 | 9.391 | 0 | 0.3099
12 |  | 1.03 | 32 | 1.556 | 1 | flow tee | 0.9 | 0.11117 |  |  | 0.11117 | 0
13 |  | 1.17 | 32 | 1.779 |  |  |  | 0 | 18.4 | 11.919 | 0 | 2.1931
13 |  | 1.17 | 32 | 1.779 | 1 | flow tee | 0.9 | 0.14532 |  |  | 0.14532 | 0
13 |  | 1.17 | 32 | 1.779 | 1 | elbow | 1.4 | 0.22606 |  |  | 0.22606 | 0
13 |  | 1.17 | 32 | 1.779 | 1 | reducer | 1 | 0.16147 |  |  | 0.16147 | 0
14 |  | 1.74 | 40 | 1.752 |  |  |  | 0 | 3.5 | 9.125 | 0 | 0.31938
14 |  | 1.74 | 40 | 1.752 | 1 | branch tee | 1.6 | 0.25057 |  |  | 0.25057 | 0
14 |  | 1.74 | 40 | 1.752 | 1 | reducer | 1 | 0.15661 |  |  | 0.15661 | 0
15 |  | 2.74 | 50 | 1.524 |  |  |  | 0 | 6.3 | 4.899 | 0 | 0.30864
15 |  | 2.74 | 50 | 1.524 | 1 | flow tee | 0.9 | 0.10665 |  |  | 0.10665 | 0
15 |  | 2.74 | 50 | 1.524 | 5 | elbow | 1 | 0.1185 |  |  | 0.59249 | 0
15 |  | 2.74 | 50 | 1.524 | 1 | bflow device |  | 0 |  |  | 4 | 0
15 |  | 2.74 | 50 | 1.524 | 1 | meter |  | 0 |  |  | 1.175 | 0
15 |  | 2.74 | 50 | 1.524 | 1 | ball valve | 0.17 | 0.020145 |  |  | 0.020145 | 0
[9 empty] | Pressure Loss ∑ |  | 9.0322 | 8.206 | = | Total friction losses | 17.2382
[14 empty] | Elevation pressure loss | 19.5 | from Figure 1
[14 empty] | Elevation pressure gain | 0
[14 empty] | Total pressure loss/gain | 36.7382 | at flow | 2.74 L/s
[14 empty] | Mains pressure | 60
[14 empty] | Pressure required at outlets | 40
[14 empty] | Residual pressure at flow | -16.7382
Residual pressure negative
Pumping solution required